| Building name: |  |  |  | Reference No. |  | Rev-00A |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Functional Critical Planned Maintenance BMS System |  |  |  |  |  |  |  |  |  |
| Sr. No. | Item | Frequency (FQ) | Action |  | Notes | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  |  |  | N/A | Yes | No |  |
| 1 | Supervisory PC/Micro based system |  |  |  |  |  |  |  |  |  |  |  |  |
| 1.1 | Diagnostic routine on computer (where appropriate) | Biannual | Perform diagnostic tasks and check computer operation |  | This routine will check all aspects of computer hardware and software |  |  |  |
| 1.2 | Clock and Calendar | Biannual | Check real-time clock and date settings |  |  |  |  |  |
| 1.3 | Cooling Fans | Biannual | Check condition, clean and lubricate if necessary |  | Do not lubricate if sealed for life bearings. Wipe off any excess lubricant as it will attract dust which will stick to it |  |  |  |
| 1.4 | Filters | Biannual | Check condition, clean and lubricate if necessary |  |  |  |  |  |
| 1.5 | Software Archives | Biannual | take back up copy of site-specific data files verify operating programs and functionality |  | Ensure that security is retained and that any updating of files is incorporated. It is recommended that a copy of the back-up data is stored in a fireproof safe or off-site |  |  |  |
| 1.6 | Cables and Connectors | Annual | Check security, integrity and for physical damage |  |  |  |  |  |
| 1.7 | Discs and Drives | Annual | Clean according to the manufacturer's instructions |  |  |  |  |  |
| 1.8 | Clock Battery | Annual | Check and replace, if necessary |  | Battery disposal should be in accordance with regulation and environmental requirements |  |  |  |
| 1.9 | Mouse | Annual | Check for smooth operation and clean ball as necessary |  | More frequent cleaning can be implemented, if needed |  |  |  |
| 1.10 | Visual Display Unit (VDU)/Monitors | Annual | Check: Focus Contrast Brightness For correct operation |  |  |  |  |  |
| 1.11 | Keyboard | Annual | Check for correct operation and clean |  |  |  |  |  |
| 1.12 | Cleaning | Annual | Clean with approved cleanser |  | Treat with anti-static compound. Depending on use and location, more frequent cleaning may be necessary |  |  |  |
| 1.13 | Cables and Connectors | Annual | Check security, integrity, and for physical damage |  |  |  |  |  |
| 1.14 | Cleaning | Annual | Use recommended cleaning agent |  | Remove paper or tape debris |  |  |  |
| 1.15 | Test Sequence | Annual | Check, adjust and replace if necessary: Paper feed Transport system Printer cartridge |  |  |  |  |  |
| 1.16 | Consumables (Wherever applicable) | Annual | Clean stocks |  |  |  |  |  |
| 2. |  |  |  |  |  |  |  |  |  |
| 2.1 | Data Communications | Annual | Check integrity of data flow in both directions |  | If more than one path exists, all must be verified |  |  |  |
| 2.2 | Central Station units | Annual | Check operation and visually inspect. Check if environmental conditions of all equipment are within prescribed limits |  | To include modems, line drivers, telemetry cables, and interface units |  |  |  |
| 2.3 | Central Station/ Outstations | Annual | Check integrity of data flow in both directions |  | If more than one data path exists, all must be verified. Caution ‒ there may be interaction with specialist applications |  |  |  |
| 2.4 | Connectors | Annual | Check security, integrity, and for damage |  |  |  |  |  |
| 2.5 | Alarms Receiving | Annual | Confirm that all critical alarms are received by the central supervisor. Check spurious alarms and report faults (as incurred) |  |  |  |  |  |
| 2.6 | Alarms Generating | Annual | Check generation of alarms from all input and output devices |  |  |  |  |  |
| 2.7 | Network | Annual | Check communications between central supervisory computer and outstations and other networked devices |  |  |  |  |  |
| 3. |  |  |  |  |  |  |  |  |
| 3.1 | Outstation Hardware | Annual | Check mechanical and environmental condition |  | Environmental conditions, e.g. temperature and humidity should be within manufacturer's recommended limits |  |  |  |
| 3.2 | Connectors | Annual | Check security, integrity, and for damage |  | Includes security of incoming cables, prevention of ingress of moisture, door seals etc. |  |  |  |
| 3.3 | Power Supplies | Annual | Carry out voltage check on all power supplies |  | Check automatic restart/rebooting of software program |  |  |  |
| 3.4 | Stand-by batteries/Uninterruptible Power Supplies (UPS) | Annual | Check against manufacturer's specification. Replace as necessary |  |  |  |  |  |
| 3.5 | Digital Inputs | Annual | Check by activating sensing/control devices in field |  | Care shall be taken to isolate local operation |  |  |  |
| 3.6 | Digital Outputs | Annual | Check operation of output stopping by operating routine (where appropriate). Check switching by software interlocks. |  |  |  |  |  |
| 3.7 | Analogue Inputs | Annual | Read and check calibration of analogue inputs |  |  |  |  |  |
| 3.8 | Analogue Outputs | Annual | Check for accuracy of output signal |  |  |  |  |  |
| 3.9 | Manual Override (Physical) | Annual | Check status |  | Review, Record, and Report |  |  |  |
| 3.10 | Installed Program | Annual | Check integrity, alarms, interlocks, optimization |  |  |  |  |  |
| 4 |  |  |  |  |  |  |  |  |  |
| 4.1 | Control Loops | Biannual | Check integrity of the installed program. Check sequence, operation of control, outputs and check stability of plant. Undertake as necessary fine tuning of control loops. Adjust settings in conjunction with the building manager to achieve the required internal environmental conditions |  | Frequency should be agreed with client. This action should be related to the critical nature of the operation |  |  |  |
| 4.2 | Optimized Start/Stop | Annual | Verify operation by interrogating software/hardware copy |  | Building layouts and occupational requirements are seldom of a static nature. Therefore, control strategies and their suitability need to be reassessed on a regular basis |  |  |  |
| 4.3 | Time Clock | Annual | Check real time clock and date for accuracy throughout system |  |  |  |  |  |
| 4.4 | Time Switching | Annual | Review current operating parameters according to site needs |  | e.g. Time settings and schedules |  |  |  |
| 4.5 | Data Logging | Annual | Review need for existing data logs. Delete/archive logs as required |  | Report to Management on the need to review existing arrangements |  |  |  |
| 4.6 | Alarm - faults, out of limit alarms | Annual | Check that plant alarms and software interlocks with safety implications are operating correctly. Check alarm priorities, routings, and reactions. Check alarm priorities are appropriate |  | The checking of possible reactions to certain critical alarms and programs must be carefully coordinated with other trades and building tenants. Where there are safety implications, verify alarm integrity. Review system of reporting outstanding alarm conditions and report discrepancies |  |  |  |
| 4.7 | Alarm Management and Report | Annual | Review frequencies of generated alarms. Review alarm log records for indication of untoward conditions |  | Report and record if any non-conformance, as appropriate |  |  |  |
| 4.8 | Power Failure and Restoration | Annual | Check plant startup/shutdown sequence and integration with other assets according to the logic |  | Report and record if any non-conformance, as appropriate |  |  |  |
| 4.9 | Generator loading program | Annual | Check plant startup/shutdown sequence and integration with other assets according to the logic |  | Report and record if any non-conformance, as appropriate |  |  |  |
| 4.10 | Maximum demand/load shedding | Annual | Check plant startup/shutdown sequence and integration with other assets according to the logic |  | Report and record if any non-conformance, as appropriate |  |  |  |
| 4.11 | Load Cycling | Annual | Check operation |  | Report and record if any non-conformance, as appropriate |  |  |  |
| 4.12 | Software Interlocks | Annual | Check and verify operation |  | Report and record if any non-conformance, as appropriate |  |  |  |
| 4.13 | Manual status review/function | Annual | Check manual overrides and effect on system and effect on system operation |  | At site level, review parameters, lockouts, changes, all points in manual override, and forced analogue values. Review findings with client |  |  |  |
| 4.14 | Outstations | Biannual | Back up all outstation files. Make two copies. Store one onsite and one offsite |  |  |  |  |  |
| 4.15 | O&M | Annual | Advise where control strategy descriptions in operating and maintenance manuals are incorrect. Ensure, where appropriate, additional documentation meets all quality assurance procedures |  |  |  |  |  |
| 4.16 | Schematics | Annual | Check schematics indicate correctly |  |  |  |  |  |
| 4.17 | Logbooks | Daily | Maintain a logbook of all changes made to the system |  | As necessary to the site-specific requirements |  |  |  |

| 13.0 | Specific Preventive Maintenance Notes |  |  |  |
| --- | --- | --- | --- | --- |

| No. | Reviewer’s Comments | Resolution |
| --- | --- | --- |
|  | Originator’s Name/Signature and Date: | Checker’s Name/Signature and Date: |