| PROJECT NAME: |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | INSPECTION ITEM |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  | N/A | YES |  | NO |
| CAUTION: SPACE HEATERS MAY BE ENERGIZED |  |  |  |  |  |  |  |
|  | Equipment is de-energized, safe and locked-out. |  |  |  |  |  |  |
|  | Equipment is identified and tagged correctly in accordance with design layout drawings. |  |  |  |  |  |  |
|  | Equipment is undamaged, positioned, aligned correctly and securely bolted. |  |  |  |  |  |  |
|  | Equipment compartments are accessible and doors operate freely with adequate clearance. |  |  |  |  |  |  |
|  | Panel interiors are clean and door seals are clean and free of tears or damage. |  |  |  |  |  |  |
|  | Panel doors are closed and secured with appropriate bolting/closure mechanisms. |  |  |  |  |  |  |
|  | Breaker nameplate data is in agreement with load requirements. |  |  |  |  |  |  |
|  | Equipment is grounded in accordance with project specifications including ground connection to ground bus. |  |  |  |  |  |  |
|  | Panel interior components are securely installed and undamaged. |  |  |  |  |  |  |
|  | Panel front mounted components, indicators, lamps and meters are securely mounted, undamaged and correctly labeled. |  |  |  |  |  |  |
|  | Lock devices are fitted to support LOTO (lock out/tag out) activities. |  |  |  |  |  |  |
|  | Gland plates and terminations are correct and suitable for external cables. |  |  |  |  |  |  |
|  | Bus bars are clean and clear of debris and torqued to specifications (torques records available). |  |  |  |  |  |  |
|  | Shipping split terminations are complete (wiring and bus bars). |  |  |  |  |  |  |
|  | Shipping blocks and temporary ground straps are removed. |  |  |  |  |  |  |
|  | Cables are terminated, clearly identified/labeled, loomed and segregated in accordance with project specifications. |  |  |  |  |  |  |
|  | Fuses are installed or available. |  |  |  |  |  |  |
|  | Special tools, including racking grounding devices, are available. |  |  |  |  |  |  |
|  | Safety signs (coordinated with ESH and construction) are fixed at appropriate locations and contact numbers are displayed for emergency notification. |  |  |  |  |  |  |
|  | Shock hazard and Arc Flash labels are applied to equipment. |  |  |  |  |  |  |
|  | Arc flash Limited Approach Boundary (LAB) is identified by markings or signage. |  |  |  |  |  |  |
|  | Single line drawings of station distribution are wall mounted/available in electrical distribution rooms/areas. |  |  |  |  |  |  |
|  | Adequate lighting is in operation. |  |  |  |  |  |  |
|  | Appropriate fire extinguishers are available. |  |  |  |  |  |  |
|  | Appropriate Arc Flash PPE is available to support energized testing/operation activities. |  |  |  |  |  |  |
|  | Produce punch list items for identified defects. |  |  |  |  |  |  |
| No. | Reviewer's Comments | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |