| PROJECT NAME: |  |  | DRAWING NO. |  |  | REV. |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| No. | INSPECTION ITEM |  |  | CHECKED SATISFACTORY |  |  |  |
|  |  |  |  | N/A | YES |  | NO |
|  | General |  |  |  |  |  |  |
|  | All packing materials and restrains has been removed from each cabinet. |  |  |  |  |  |  |
|  | UPS Main breaker coordination study has been completed prior to acceptance. |  |  |  |  |  |  |
|  | Each cabinet in the UPS system is placed in its installed location. |  |  |  |  |  |  |
|  | All cabinets except standalone cabinets are bolted together. |  |  |  |  |  |  |
|  | Grounding bond is installed between all cabinets that are bolted together. |  |  |  |  |  |  |
|  | All switchboards, conduits, and cables are properly routed to the UPS and auxiliary cabinets. |  |  |  |  |  |  |
|  | Power cables are terminated on by-pass terminals. |  |  |  |  |  |  |
|  | Power cables are terminated on the input breaker. |  |  |  |  |  |  |
|  | Aground conductor is properly installed. |  |  |  |  |  |  |
|  | If neutral is used, no other neutral to ground bonds exist downstream of the UPS. |  |  |  |  |  |  |
|  | Battery cables and harness are terminated on the battery contactor. |  |  |  |  |  |  |
|  | Internal battery cabinet connections have been completed (bus bars, plugs, etc.). |  |  |  |  |  |  |
|  | Air conditioning equipment is installed and operating properly. |  |  |  |  |  |  |
|  | The area around the installed UPS is clean and dust free. |  |  |  |  |  |  |
|  | Adequate workspace exists around the UPS and other cabinet. |  |  |  |  |  |  |
|  | Adequate lighting is provided around all UPS equipment. |  |  |  |  |  |  |
|  | Insulation resistance and continuity testing conducted on bus bars and results are satisfactory. |  |  |  |  |  |  |
|  | Labelling provided in cables, conduits, and equipment. |  |  |  |  |  |  |
| 19 | Inspect batteries for physical damage or defects |  |  |  |  |  |  |
| 20 | Match nameplate of batteries with required Specifications |  |  |  |  |  |  |
| 21 | Assure all battery connections are clean and free for rust |  |  |  |  |  |  |
| 22 | Assure all cells are properly numbered |  |  |  |  |  |  |
| 23 | Assure all cells protective covers are installed |  |  |  |  |  |  |
| 24 | Assure all tools and accessories for battery maintenance are available |  |  |  |  |  |  |
| 25 | Assure battery room ventilations and exhaust systems are functioning per design and volume of the battery system |  |  |  |  |  |  |
| 26 | Assure the installation of the safety systems (Eyes wash, showers, warning stickers etc.) in the battery rooms |  |  |  |  |  |  |
| 27 | For flooded lead acid racks check for specific gravity and liquid level |  |  |  |  |  |  |
| 28 | Assure all batteries all securely grounded |  |  |  |  |  |  |
| 29 | Assure the battery bank has a disconnect switch easily accessible |  |  |  |  |  |  |
| No. | Reviewer's Comments | Resolution |  |  |  |  |  |
| Originator's Name / Signature and Date: |  | Checker's Name / Signature and Date: |  |  |  |  |  |