The below schedule is a sample of planned maintenance activities, however, The Entity shall proactively source from the manufacturer, the required maintenance for each assets.

| Building Name: |  |  | Reference No. |  |  | Rev-00A |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Functional Critical Planned Maintenance Communication System |  |  |  |  |  |  |  |  |
| Sr. No. | Item | Frequency (FQ) | Action |  | Notes | CHECKED SATISFACTORY |  |  |
|  |  |  |  |  |  | N/A | Yes | No |
| 1.1 | Diagnostic Routine on Computer (where appropriate) | Biannual | Perform diagnostic tasks and check computer operation |  | This routine will check all aspects of computer hardware and software |  |  |  |
| 1.2 | Wireless Systems | 6 Monthly | Clean and examine bells, buzzers, pull cords, pushes, indicators, relays, contact boxes fuses. Ensure terminal connections are sound |  | Visually inspect printed circuit boards. Clean, examine, and test all components of the system and reset as required. Examine antennae |  |  |  |
| 1.3 | System Checks | 6 Monthly | Clean, examine and test all components of the system and reset as required. Examine antennae |  |  |  |  |  |
| 1.4 | Batteries | 6 Monthly | Test dry batteries, renew as necessary, and ensure their security |  |  |  |  |  |
| 1.5 | Filters | Biannual | Check condition, clean and lubricate, if necessary |  |  |  |  |  |
| 1.6 | Software Archives | Biannual | Take back-up copy of site-specific data files. Confirm operating programs and functionality |  | Ensure that security is retained and that any updating of files is incorporated. It is recommended that a copy of the back-up data is stored in a fireproof safe or off-site |  |  |  |
| 1.7 | Cables | Annual | Check security, integrity, and for physical damage |  |  |  |  |  |
| 1.8 | Discs and Drives | Annual | Clean according to the manufacturer's instructions |  |  |  |  |  |
| 1.9 | Clock Battery | Annual | Check and replace, if necessary |  | Battery disposal should be in accordance with regulation and environmental requirements |  |  |  |
| 1.10 | Connectors | Annual | Check connectors for security and integrity |  |  |  |  |  |
| 1.11 | Mouse | Annual | Check for smooth operation and clean ball as necessary |  | More frequent cleaning can be implemented, if needed |  |  |  |
| 1.12 | Visual Display Unit (VDU)/Monitors | Annual | Check: Focus Contrast Brightness For correct operation |  |  |  |  |  |
| 1.13 | Keyboard | Annual | Check for correct operation and clean |  |  |  |  |  |
| 1.14 | Cables and Connectors | Annual | Check security, integrity, and for physical damage |  |  |  |  |  |
| 1.15 | Cleaning | Annual | Use recommended cleaning agent |  | Remove paper or tape debris |  |  |  |
| 1.16 | Data Communications | Annual | Check integrity of data flow in both directions |  | If more than one path exists, all must be verified |  |  |  |
| 1.17 | Closed Circuit Television (CCTV) System check | Twice Annually | Check systems for functionality and operability |  |  |  |  |  |
| 1.18 | Connectors | Annual | Check security, integrity, and for damage |  |  |  |  |  |
| 1.19 | Remote Video Response Centre | Twice Annually | Checks to confirm remote operation |  |  |  |  |  |
| 1.20 | Lift Auto Dialer | Every three days checks | Input signal of alarm checks |  |  |  |  |  |
| 1.21 | Alarms Receiving | Annual | Confirm that all critical alarms are received by the central supervisor. Check spurious alarms and report faults (as incurred) |  |  |  |  |  |
| 1.22 | Alarms Generating | Annual | Check generation of alarms from all input and output devices |  |  |  |  |  |
| 1.23 | Network | Annual | Check communications between central supervisory computer and outstations, and other networked devices |  |  |  |  |  |
| 1.24 | Outstation Hardware | Annual | Check mechanical and environmental condition |  | Environmental conditions, such as temperature and humidity should be within the manufacturer's recommended limits |  |  |  |
| 1.25 | Connectors | Annual | Check security, integrity, and for damage |  | Includes security of incoming cables, prevention of ingress of moisture, door seals |  |  |  |
| 1.26 | Digital Inputs (DIs) | Annual | Check by activating sensing/control devices in field |  | Care shall be taken to isolate local operation |  |  |  |
| 1.27 | Digital Outputs (Dos) | Annual | Check operation of output stopping by operating routine (where appropriate). Check switching by software interlocks |  |  |  |  |  |
| 1.28 | Vented Batteries | Quarterly | Vented batteries should be examined to ensure that the specific gravity of each cell is correct |  | Electrolyte levels should be checked and topped up as necessary, and the specific gravity of the electrolyte in each cell should be checked to ensure that it is correct |  |  |  |
| 1.29 | User Checks –Outstation | Weekly | An outstation should be operated |  | It should be confirmed that the call is correctly received at the master station |  |  |  |
| 1.30 | User Checks –Master Station | Weekly | In premises in which the location of the master station is such that the audible fault warning signal could go unnoticed for longer than 24 hours |  | A special check should be carried out each day to confirm that either the equipment indicates normal operations or that any fault indication is receiving necessary attention |  |  |  |
| 1.31 | Analogue Inputs | Annual | Read and check calibration of analogue inputs |  |  |  |  |  |
| 1.32 | Analogue Outputs | Annual | Check for accuracy of output signal |  |  |  |  |  |
| 1.33 | Installed Program | Annual | Check integrity, alarms, interlocks, and optimization |  |  |  |  |  |
| 1.34 | Time Clock | Annual | Check real time clock and date for accuracy throughout system |  |  |  |  |  |
| 1.35 | Time Switching | Annual | Review current operating parameters according to site needs |  | For example, Time settings and schedules |  |  |  |
| 1.36 | Data Logging | Annual | Review the need for existing data logs. Delete/archive logs as required |  | Report to Management on the need to review existing arrangements |  |  |  |
| 1.37 | Alarm Management and Report | Annual | Review frequencies of generated alarms. Review alarm log records for indication of untoward conditions |  | Report and record if any non-conformance, as appropriate |  |  |  |
| 1.38 | Software Interlocks | Annual | Check and confirm operation |  | Report and record if any non-conformance, as appropriate |  |  |  |
| 1.39 | Electrical Test on Communication Systems | 3 Yearly | Carry out a periodic inspection with associated circuit tests in accordance with BS7671 |  |  |  |  |  |
| 1.40 | Communication Rooms and Server Rooms CO2 and Inert Gas Systems | 6 Monthly | Panel Test, Inspect, and Test and Enclosure integrity |  |  |  |  |  |
| 1.41 | CCTV | Annually | Inspection and testing of all associated equipment | Full inspection and testing. Written records including date of test, next test date, defects found, and record of repairs |  |  |  |  |
| 1.42 | Testing of Sounders and Call Points |  | Activation of manual call point to confirm system operations of the indicative equipment |  |  |  |  |  |
| 1.43 | Security/Access Systems | Annually | Carry out a full test, inspection, service, and maintenance of system |  |  |  |  |  |
| 2.0 | Specific Planned Maintenance (PM) Notes |  |  |  |  |  |  |  |
| - No. | - Reviewer’s Comments |  |  | - Resolution |  |  |  |  |
|  | Originator’s Name/Signature and Date: |  |  | Checker’s Name/Signature and Date: |  |  |  |  |

Table 5