| No. | INSPECTION ITEM | Task |  | Frequency | CHECKED SATISFACTORY |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  | N/A | YES |  | NO |
| 1.0 | DAM EMBANKMENT |  |  |  |  |  |  |  |
| 1.1 | Vegetation Control | Cut grass at least twice annually or more frequently to allow for visual surveillance of the embankment surfaces |  | Biannually* |  |  |  |  |
| 1.2 | Maintain Crest and Roadway | Seal road cracks resulting from normal wear and aging Maintenance of expansion joints at Crest |  | Annually* |  |  |  |  |
| 1.3 | Maintain Crest Design Elevation | Maintain the design elevation of unimproved crest surfaces by leveling and grading the crest to design specifications Fill any ruts or minor depressions |  | Annually* |  |  |  |  |
| 1.4 | Maintain Upstream and downstream Slope Protection | Repair of riprap by regarding the slope to original lines and replacing the bedding material and riprap Repair voids in the riprap by adding or moving riprap |  | Annually* |  |  |  |  |
| 1.5 | Erosion Control on Downstream Face | Repair erosion gullies by removing loose materials and replacing them with compacted fill |  | Annually* |  |  |  |  |
| 2.0 | CONCRETE ELEMENTS/ ONCRETE SPILLWAYS |  |  |  |  |  |  |  |
| 2.1 | Maintain Concrete Features** | Make repairs to concrete surfaces and joints, including: Patching spalled areas with a bonding agent Strengthening areas by applying coatings or by adding reinforcements Repairing corroded areas by Cathodic protection, where applicable Repairing minor cracks with an adhesive or epoxy injection Keeping concrete joints and surfaces free of vegetation |  | Annually* |  |  |  |  |
| 2.2 | Spillway Channel | Remove any obstructions/vegetation or debris from the spillway channel |  | Weekly* |  |  |  |  |
|  |  | Keep drains free and clear. Periodically rod and ream internal drains to keep them functioning |  | Monthly* |  |  |  |  |
| 2.3 | Return Channel | Remove obstructions within the return channel |  | Monthly* |  |  |  |  |
| 3.0 | EARTHEN SPILLWAY CHANNEL |  |  |  |  |  |  |  |
| 3.1 | Erosion Control | Repair erosion gullies by removing loose materials and replacing them with compacted fill Gravel and cobbles or planted grass should be added, as appropriate to the damaged area to prevent future erosion |  | Annually* And After Floods |  |  |  |  |
| 3.2 | Maintain Spillway Channel | Remove any obstructions, vegetation or debris from the Spillway channel |  | Weekly* |  |  |  |  |
|  |  | Cut grass Remove small trees and bushes that would affect flows now or in the future if let to grow |  | Annually* |  |  |  |  |
| 4.0 | DROP INLET SPILLWAY |  |  |  |  |  |  |  |
| 4.1 | Clean Trash rack | Remove all floating logs and debris from trash rack and spillway opening |  | Weekly* |  |  |  |  |
| 4.2 | Clear Air Vent(s) | Clear debris from air vent entrance |  | Monthly* |  |  |  |  |
| 4.3 | Inspect and Maintain Log boom | Replace waterlogged or submerged log boom members Repair or replace loose or missing anchors |  | Biannually* |  |  |  |  |
| 4.4 | Inspect and Repair Concrete elements, joints and Riser | Concrete Elements: Make repairs to concrete surfaces and joints (Refer to Section 2.1 in the Attachment 1 on maintaining concrete features) |  | Annually* |  |  |  |  |
| 4.5 | Maintain Metal Features | Remove mineral deposits and paint metal features Inspect the Cathodic protection. Restore corroded metal to original condition by welding on new metal Paint the metal surface and apply protection system |  | Annually* |  |  |  |  |
| 5.0 | OUTLET WORKS |  |  |  |  |  |  |  |
| 5.1 | Gates and Valves | Test gates and valves for proper operation and leakage |  | Annually* |  |  |  |  |
|  |  | Gates and valves are to be maintained according to the manufacturers' instructions Follow the guidelines specified by the manufacturer |  | As Specified* |  |  |  |  |
| 5.2 | Gate and Valve Controls | Follow guidelines specified by manufacturer |  | As Specified* |  |  |  |  |
| 5.3 | Intake Structure | Lower reservoir level or hire divers to inspect intake for low-level outlet works Clear debris from trash rack Apply protective coating to - Metalwork Repair concrete, as needed |  | 5 Years* |  |  |  |  |
| 5.4 | Conduit | Visually inspect conduit from downstream end for corrosion, leakage, or other significant problems |  | Annually* |  |  |  |  |
|  |  | Inspect entire conduit interior either manually or via remote control camera Repair or reline as needed |  | 5 Years* |  |  |  |  |
| 12.0 | SPECIFIC PPM NOTES |  |  |  |  |  |  |  |
|  | * Task nature and frequency to be determined by site-specific risk assessment - depends inter alia upon materials, exposure, and location. **Get appropriate advice and assistance from qualified and competent personnel before making repairs to concrete surfaces and joints. Concrete problems may be an indication of a serious dam safety problem. Also, report any new or changing (increasing or decreasing) cracks. |  |  |  |  |  |  |  |
| No. | Reviewer's Comments |  | Resolution |  |  |  |  |  |
| Originator's Name/Signature and Date: |  |  | Checker's Name/Signature and Date: |  |  |  |  |  |