An example Task Instruction Sheet for HVAC Systems is featured below. The Entity should use it as a basis by which to develop its own site-specific Task Instruction Sheets for HVAC Systems.

Skill Types

ME	–	Mechanical Engineer

EE	–	Electrical Engineer

IC	–	Instrumentation and Control Engineer

CE	–	Civil Engineer

HVAC System

| HVAC Systems Terminal Unit FCU |  |  |  |
| --- | --- | --- | --- |
| Item | FQ | Action | Skill Level |
| Status | 6M | Switch off and isolate | ME |
| Condensate Drain Connection and Pump |  | Check connection is clear. Ensure condensate lift pump is operational and able to discharge condensate to the drainage pipework |  |
| Permanent Filters |  | Clean and refit, ensuring proper location |  |
| Disposable Type Filters |  | Replace, ensuring proper location |  |
| Test Unit |  | Restore power supply and run unit. Check airflow is normal at correct speed setting |  |
| Casing |  | Cleaning |  |
| Ductwork Flexible Couplings (if fitted) | 12M | Check condition. Repair/reattach any ductwork to the spigots as necessary |  |
| Grilles and Diffusers |  | Clean using vacuum or alternatively, remove, and clean |  |
| Strainers |  | Inspect and clean strainers as necessary |  |
| Chilled Water/LPHW control Valves | 6M | Check functioning |  |
| Thermostats | 12M | Check operation by moving set point. Restore to original setting |  |
| HVAC System - Active Chilled Beams |  |  |  |
| Active Chilled Beams | 12M | The frequency of cleaning will be driven by the environment in which the beams are installed and the filter level in the AHU and this should be reviewed on a site-by-site basis | ME |
| Heating and Cooling Coil |  | Vacuum all dirt clear to ensure air has a free path through the exchanger for maximum performance. If the fins are damaged, comb back into shape |  |
| Air Connection Spigot |  | Check the air connection spigot is secure |  |
| Unit Diffuser |  | Clean the unit with a cloth wetted with detergent diluted with water |  |
| Control Valve |  | Check the operation of both the cooling and heating (as applicable) control valves. Take note of any signs of leaking and correct and/or report as appropriate |  |
| Hoses |  | Check condition and report any signs of rusting or leakage |  |
| HVAC System - Passive Chilled Beams |  |  |  |
| Active Chilled Beams | 12M | The frequency of cleaning will be driven by the environment in which the beams are installed and this should be reviewed on a site by site basis | ME |
| Item |  | Action |  |
| Heating and Cooling coil |  | Vacuum all dirt clear to ensure air has a free path through the exchanger for maximum performance. If the fins are damaged, comb back into shape |  |
| Unit Diffuser Panel |  | Clean the unit with a cloth wetted with detergent diluted with water |  |
| Control Valve |  | Check the operation of both the cooling and heating control valves, as applicable. Take note of any signs of leaking and correct and/or report as appropriate |  |
| Hoses |  | Check condition and report any signs of rusting or leakage |  |