| System | Description of test | Frequency |  |  |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Daily | Weekly | Monthly | Annual |  |
| Fire Detections | Sounder Test |  | X |  |  |  |
| Fire doors Hold Backs | Check release upon activation |  | X |  |  |  |
| Fire Escape routes / final exit | Check clear of obstruction | X |  |  |  |  |
| Stair Pressurization system | Check fans run on Activation |  |  | X |  |  |
| Elevators | Check proceed to Escape level and doors open |  | X |  |  |  |
| Security Barriers | Check that all open upon activation |  | X |  |  |  |
| Escalators & Moving walkways | Check that they come to stop |  | X |  |  |  |
| Emergency Generator | Operate generator OFF LOAD for maximum of 15 minutes |  |  | X |  |  |
| Emergency Generator | Carry out ON LOAD test of Generator with building or Emergency load |  |  |  | X |  |
| Emergency Lighting | Operate lights for short period to ensure remain illuminated |  |  | X |  |  |
| Emergency lighting | Operate Lighting for full 3 Hour duration test |  |  |  | X |  |
| Sprinkler Pumps | Undertake 'Bell Test' of sprinklers and record cut in pressure |  | X |  |  |  |
| Dry Riser | Check all landing valves and caps are in place |  |  | X |  |  |
| Dry Riser | Check using system pressure and drain down on completion |  |  |  | X |  |
| Fire Dampers | Check operation of fire dampers (visually or confirmation on BMS |  |  | X |  |  |
| Plant & Equipment | Check associated plant shutters down in the event of a fire activation (AHU/TEF/ Kitchen fans) |  |  | X |  |  |
| Fire suppression system | Check panel outputs to 'House Alarm' |  |  | X |  |  |
| Fire Suppression Bottle storage | Check system pressure within limits |  |  | X |  |  |
| Fire Extinguishers check | Check in correct location pins in place and pressure correct |  |  | X |  |  |
| Fire Extinguishers check | Carry out Annual Maintenance |  |  |  | X |  |
| PAVA System Check | Operate TEST message where fitted |  | X |  |  |  |
| PAVA- Carry out dBA test of speakers | Undertake test using calibrated meter of speakers to meet designed output |  |  |  | X |  |