An example Task Instruction Sheet for Boiler Systems is featured below. The Entity should use it as a basis by which to develop its own site-specific Task Instruction Sheets for Mechanical Systems.

Skill Types

ME	–	Mechanical Engineer

EE	–	Electrical Engineer

IC	–	Instrumentation and Control Engineer

CE	–	Civil Engineer.

| Boiler Systems |  |  |  |
| --- | --- | --- | --- |
| Item | FQ | Action | Skill Types |
| Water gauge test | Daily | NA | ME |
| Water level left and right hand gauge |  | Manual blow down | ME |
| Water Level Control |  | Test low water level cut-out and lock-out. | ME |
| Feed pump start/stop or modulation |  | Check operation | ME |
| Pressure readings |  | Record the pressure gauge reading | ME |
| PH and TDS water Test |  | Carry out TDS water quality test, record the result and make Adjustments where necessary | ME |
| Blow Down |  | Record quantity of water blown down. | ME |
| Feed water and condensate check |  | Check the feed tank level is adequate and there are no contaminants. Check that the chemical dose metering device is functioning and there are adequate chemical stocks in the tanks. Check that the in-house routine sample results are within their given parameters provided by the water treatment specialist and take remedial action when necessary. Check the temperature is above the required level for the treatment doses specified for oxygen scavenging. | ME |
| Flame failure | Weekly | Test flame failure lock-out. This may not be present on non-self-monitoring boilers | ME |
| Failure to ignite. |  | Test failure to ignite lock out | ME |
| Water level 1st. |  | Test by lowering water level to 1st low water level, by evaporation and controlled blowdown, and check burner locks out and the alarm is sounded | ME |
| Water level 2nd. |  | Test by lowering water level to 2nd low water level, by evaporation and controlled blowdown, and check burner locks out and the alarm is sounded | ME |
| Isolation from electricity supplies | Monthly | Switch and lock off. Remove fuses from both supplies. | ME |
| Water treatment |  | Ask if the system has been drained since last visit and if it was retreated with inhibitor. | ME |
| Water checks |  | Leakage checks | ME |
| Fan cooling air duct |  | Remove button front casing clean duct through casing, remove the rear end fan motor which is exposed when the casing is removed. | ME |
| Drain pipe | Annual | Check for free flow, actuate main drain if necessary | ME |
| Boiler circulated water. |  | Test for correct conductivity at 20/25º C. | ME |
| Boiler sequence |  | Replace all covers and reinstate electrical supply | EE |
| Load control system |  | Examine mechanism and lubricate | EE |