An example task instruction sheet for security systems is featured below. The Entity shall use it as a basis by which to develop its own site specific task instruction sheets for maintenance of security systems.

Skill Types

- Specialist Engineer (SE) (Security Systems)

- Extra Low Voltage (ELV)

- Maintenance Engineer (ME)

| Item | FQ | Action | Skill Level |
| --- | --- | --- | --- |
| Electronic Security Systems (ESS) | Biannually | Check functionality of primary and secondary drive | SE |
| Primary drive and secondary drive |  |  |  |
| Visually inspect system connections |  | Conduct physical inspection of all terminals |  |
| System faults |  | Check for system faults |  |
| Hard disks |  | Check space in hard disk |  |
| Delete/Archive log files as necessary |  | Check for unwanted files and archive |  |
| Clean Monitor Screen | Annually | Clean screens |  |
| Complete a data archive |  | Check and archive irrelevant data as applicable |  |
| Complete hard drive defragmentation |  | Integration check, layout of files. Do process run as necessary |  |
| Verify operating systems file integrity | Biannually | Check for corrupted files, database, software files |  |
| Verify Program File Integrity | Biannually |  |  |
| Verify data file integrity | Annually | Follow manufacturer step by step instructions to perform these checks | SE |
| Perform a virus scan |  |  |  |
| Authenticate system operators and privileges |  |  |  |
| Check field panel communications |  |  |  |
| Inspect field panel wiring and connections |  |  |  |
| Workstations, CPU, and UPS are clean and without any trouble |  |  |  |
| Ports connectivity/Ethernet Switches |  |  |  |
| Sensors and controllers are healthy and functioning |  |  |  |
| Hardware communication with server |  |  |  |
| Access Control System |  |  |  |
| Batteries | Annually | Test field panel battery levels | SE |
| Power Supply | Annually | Check function |  |
| Key | Annually | Check function |  |
| Magnetic Stripe | Annually | Check function |  |
| Readers | Annually | Check card reader operations |  |
| RFID card | Annually | Check function |  |
| Biometric | Annually | Check function |  |
| Position Sensors | Annually | Check function |  |
| Electric latch | Annually | Check function |  |
| Electric Lock | Annually | Check function |  |
| Electromagnetic lock | Annually | Check function |  |
| Manual/Auto Operation | Annually | Check function |  |
| Electric hardware | Biannually | Clean, lubricate, and adjust locks |  |
|  | Biannually | Verify door contact operation |  |
|  | Biannually | Inspect, clean, and adjust card printers |  |
|  | Biannually | Inspect, clean, and adjust image capture camera |  |
| CCTV Surveillance Systems |  |  |  |
| Visually inspect CCTV monitor image quality | Monthly | Conduct Visual Inspection | ME |
| Visually inspect CCTV recording equipment | Monthly | Conduct Visual Inspection | ME |
| Inspect video record and playback operations | Monthly | Conduct Visual Inspection | ME |
| Check CCTV system switcher operation | Weekly | Conduct Visual Inspection | ME |
| Cameras primary input power | Weekly | Conduct Visual Inspection | ME |
| Video signal transmission | Weekly | Conduct Visual Inspection | ME |
| Check PTZ operation |  | Functionality of camera, left, right, up, down, zoom functions, customization | SE |
| Visually inspect CCTV system connections | Annually | Cable termination checks, POE checks, and communication ports | ME |
| Clean Monitors Screens | Monthly | Conduct inspections for cleaning and ensure displays are clear | ME |
| Inspect, clean, and adjust cameras according to facility requirements | Annually | Ensure to consider weather conditions and may more frequent checks required | ME |
| Alarming inputs | Annually | Check alarm functions | SE |
| Intruder Alarm System |  |  |  |
| System Integrity | Annually | Record and report any evidence of tampering or damage | ME |
| Sensors and contacts |  | Confirm correct operation and sensitivity, where appropriate check spatial configuration for volumetric devices |  |
| Alarm signals |  | Check response to signal at con troll panel. Reset alarm points after test |  |
| Sensor covers, terminal boxes and fixings |  | Check integrity for signs of overheating, ingress of dust and moisture. Clean internal components with soft brush and remove any dirt or fluff. When replacing covers, check operation of any tamper switches which may be fitted |  |
| Power supplies | Biannually | Check power supplies and associated batteries. Batteries should be checked for signs of leakage or corrosion | SE |
| Detection modules exterior (if applicable) | Annually | Check and adjust (if necessary) | SE |
| Detection modules interior (if applicable) | Annually | Check and adjust (if necessary) | SE |
| Batteries | Annually | Check function and state of battery charger Check battery terminals connections Check that the inter-cell connections are secure and clean | SE |
| Sealed lead acid, sealed nickel-cadmium | Triennially | Check and dispose batteries in accordance to healthcare Entity environmental regulations | SE |
| Control Panel | Annually | Check control panel internally, check all control devices, fuse bridges, and phase barriers for signs of arcing and burning. Check all indication lamps are working, replace any defective lamps Check panel/cabinet door, if securely locked, and that door protection and isolation device is operative | SE |
| External Lighting |  |  |  |
| Inspection of streetlights | Monthly | Look for breakages, wear/deterioration/signs of corrosion | ME |
|  |  | Check any missing parts, screws, covers, loose fittings | ME |
| Electrical wiring and connections | Biannually | Check the integrity and look for Sign of burn/spark, loose connection, expose cabling | ME |
|  |  | Inspect for grounding and bonding arrangements | ME |
|  |  | Check the accessibility to conductor and connections | ME |
| Security of light fittings |  | Check for cleaning, condition, and security of fittings | ME |
| Lamps/Tubes |  | Check for faulty or blackened tubes or lamps | ME |
| Controls |  | Check for functionality and correct operation of timer and sensor (if available) | ME |
| Ingress Protection (external lights) |  | Check and ensure fitting integrity is maintained | ME |
| Vehicle Blockers/Bollards |  |  |  |
| Bollard Function | Quarterly | Follow OEM inspection and maintenance guidelines | SE |
| Control Function | Quarterly |  | SE |
| Physical Conditions | Quarterly |  | SE |
| Leaks | Quarterly |  | SE |
| Cabling Connectivity | Quarterly |  | SE |
| Communication | Quarterly |  | SE |
| Sounding Devices | Annually | Check functions | SE |
| Batteries | Annually | Conduct general tests | SE |
| Off premises transmission equipment (if any) | Quarterly or by automatic monthly test | Check functions | SE |
| All interface equipment | Annually | Check functions | SE |